## Instrument Index
Tag | Loop | Instrument Type | Service | Equipment / Line | P&ID Ref | Range Min | Range Max | Units | Signal | Loop Powered | I/O Type | Fail Position | Location Note | Panel | Terminal | Rationale | Status
FS-111 | 111 | Flow switch | CH-1 evaporator flow | CH-1 inlet branch | DC-I-001 |  |  |  | Dry contact |  | DI |  | On CH-1 inlet branch | CP-1 | TB-DI1-01 | Interlock: no flow, no chiller start (freeze protection) | Approved
TT-112 | 112 | RTD Pt100 temperature transmitter, in thermowell | CH-1 evaporator leaving water temperature | CH-1 outlet branch | DC-I-001 | 0 | 20 | °C | 4-20 mA | Y | AI |  | In thermowell, tip in middle third of pipe; on CH-1 outlet branch | CP-1 | TB-AI1-01 | Chiller performance monitoring | Approved
XV-113 | 113 | On/off actuated butterfly valve | CH-1 CHW isolation valve | CH-1 inlet branch | DC-I-001 |  |  |  | 24 VDC |  | DO | FO | On CH-1 inlet branch; actuator accessible | CP-1 | TB-DO1-01 | Mode switching; isolates an offline chiller | Approved
ZSC-113 | 113 | Limit switch (closed) | XV-113 closed proof | XV-113 | DC-I-001 |  |  |  | Dry contact |  | DI |  | On XV-113 actuator | CP-1 | TB-DI1-02 | Prove the valve closed (mode switch, isolation) | Approved
ZSO-113 | 113 | Limit switch (open) | XV-113 open proof | XV-113 | DC-I-001 |  |  |  | Dry contact |  | DI |  | On XV-113 actuator | CP-1 | TB-DI1-03 | Prove the valve opened before chiller start | Approved
TT-114 | 114 | RTD Pt100 temperature transmitter, in thermowell | CH-1 evaporator entering water temperature | CH-1 inlet branch | DC-I-001 | 0 | 30 | °C | 4-20 mA | Y | AI |  | In thermowell, tip in middle third of pipe; on CH-1 inlet branch | CP-1 | TB-AI1-02 | Per-chiller delta-T and load | Approved
FS-121 | 121 | Flow switch | CH-2 evaporator flow | CH-2 inlet branch | DC-I-001 |  |  |  | Dry contact |  | DI |  | On CH-2 inlet branch | CP-1 | TB-DI1-04 | Interlock: no flow, no chiller start (freeze protection) | Approved
TT-122 | 122 | RTD Pt100 temperature transmitter, in thermowell | CH-2 evaporator leaving water temperature | CH-2 outlet branch | DC-I-001 | 0 | 20 | °C | 4-20 mA | Y | AI |  | In thermowell, tip in middle third of pipe; on CH-2 outlet branch | CP-1 | TB-AI1-03 | Chiller performance monitoring | Approved
XV-123 | 123 | On/off actuated butterfly valve | CH-2 CHW isolation valve | CH-2 inlet branch | DC-I-001 |  |  |  | 24 VDC |  | DO | FO | On CH-2 inlet branch; actuator accessible | CP-1 | TB-DO1-02 | Mode switching; isolates an offline chiller | Approved
ZSC-123 | 123 | Limit switch (closed) | XV-123 closed proof | XV-123 | DC-I-001 |  |  |  | Dry contact |  | DI |  | On XV-123 actuator | CP-1 | TB-DI1-05 | Prove the valve closed (mode switch, isolation) | Approved
ZSO-123 | 123 | Limit switch (open) | XV-123 open proof | XV-123 | DC-I-001 |  |  |  | Dry contact |  | DI |  | On XV-123 actuator | CP-1 | TB-DI1-06 | Prove the valve opened before chiller start | Approved
TT-124 | 124 | RTD Pt100 temperature transmitter, in thermowell | CH-2 evaporator entering water temperature | CH-2 inlet branch | DC-I-001 | 0 | 30 | °C | 4-20 mA | Y | AI |  | In thermowell, tip in middle third of pipe; on CH-2 inlet branch | CP-1 | TB-AI1-04 | Per-chiller delta-T and load | Approved
PT-211 | 211 | Pressure transmitter, with root valve | PCHWP-1 discharge pressure | PCHWP-1 discharge | DC-I-001 | 0 | 1000 | kPa | 4-20 mA | Y | AI |  | On PCHWP-1 discharge riser, with root valve | CP-1 | TB-AI1-05 | Pump health; proves flow | Approved
PT-221 | 221 | Pressure transmitter, with root valve | PCHWP-2 discharge pressure | PCHWP-2 discharge | DC-I-001 | 0 | 1000 | kPa | 4-20 mA | Y | AI |  | On PCHWP-2 discharge riser, with root valve | CP-1 | TB-AI1-06 | Pump health; proves flow | Approved
PT-311 | 311 | Pressure transmitter, with root valve | SCHWP-1 discharge pressure | SCHWP-1 discharge | DC-I-001 | 0 | 1000 | kPa | 4-20 mA | Y | AI |  | On SCHWP-1 discharge riser, with root valve | CP-1 | TB-AI1-07 | Pump health; proves flow | Approved
PT-321 | 321 | Pressure transmitter, with root valve | SCHWP-2 discharge pressure | SCHWP-2 discharge | DC-I-001 | 0 | 1000 | kPa | 4-20 mA | Y | AI |  | On SCHWP-2 discharge riser, with root valve | CP-1 | TB-AI1-08 | Pump health; proves flow | Approved
TCV-411 | 411 | Modulating control valve with actuator | CRAH-1 chilled water coil valve | CRAH-1 supply branch | DC-I-001 | 0 | 100 | % | 4-20 mA |  | AO | FO | On CRAH-1 supply branch | CP-1 | TB-AO1-01 | Controls CRAH-1 supply air temperature | Approved
ZT-411 | 411 | Valve position transmitter | TCV-411 position feedback | TCV-411 | DC-I-001 | 0 | 100 | % | 4-20 mA | N | AI |  | On TCV-411 actuator | CP-1 | TB-AI2-01 | Confirms the valve went where it was told | Approved
TT-412 | 412 | Duct temperature sensor, averaging element | CRAH-1 supply air temperature | CRAH-1 supply duct | DC-I-001 | 0 | 40 | °C | 4-20 mA | Y | AI |  | Downstream of coil and fan where air has mixed; averaging element | CP-1 | TB-AI2-02 | TCV-411 control variable (18°C) | Approved
TT-413 | 413 | Duct temperature sensor | CRAH-1 return air temperature | CRAH-1 return inlet | DC-I-001 | 0 | 50 | °C | 4-20 mA | Y | AI |  | At CRAH-1 return air inlet | CP-1 | TB-AI2-03 | Monitors room heat load | Approved
XS-414 | 414 | Leak detection cable with alarm relay | CRAH-1 leak detection | Floor at CRAH-1 | DC-I-001 |  |  |  | Dry contact |  | DI |  | Sensing cable on floor around CRAH-1, at low points | CP-1 | TB-DI1-07 | Water near IT equipment: highest-priority alarm | Approved
TCV-421 | 421 | Modulating control valve with actuator | CRAH-2 chilled water coil valve | CRAH-2 supply branch | DC-I-001 | 0 | 100 | % | 4-20 mA |  | AO | FO | On CRAH-2 supply branch | CP-1 | TB-AO1-02 | Controls CRAH-2 supply air temperature | Approved
ZT-421 | 421 | Valve position transmitter | TCV-421 position feedback | TCV-421 | DC-I-001 | 0 | 100 | % | 4-20 mA | N | AI |  | On TCV-421 actuator | CP-1 | TB-AI2-04 | Confirms the valve went where it was told | Approved
TT-422 | 422 | Duct temperature sensor, averaging element | CRAH-2 supply air temperature | CRAH-2 supply duct | DC-I-001 | 0 | 40 | °C | 4-20 mA | Y | AI |  | Downstream of coil and fan where air has mixed; averaging element | CP-1 | TB-AI2-05 | TCV-421 control variable (18°C) | Approved
TT-423 | 423 | Duct temperature sensor | CRAH-2 return air temperature | CRAH-2 return inlet | DC-I-001 | 0 | 50 | °C | 4-20 mA | Y | AI |  | At CRAH-2 return air inlet | CP-1 | TB-AI2-06 | Monitors room heat load | Approved
XS-424 | 424 | Leak detection cable with alarm relay | CRAH-2 leak detection | Floor at CRAH-2 | DC-I-001 |  |  |  | Dry contact |  | DI |  | Sensing cable on floor around CRAH-2, at low points | CP-1 | TB-DI1-08 | Water near IT equipment: highest-priority alarm | Approved
TT-501 | 501 | RTD Pt100 temperature transmitter, in thermowell | CHW supply header temperature | Secondary supply main (CHWS) | DC-I-001 | 0 | 20 | °C | 4-20 mA | Y | AI |  | In thermowell, tip in middle third of pipe; on secondary supply main, >= 10 pipe diameters downstream of the decoupler tee | CP-1 | TB-AI2-07 | Main control variable (8°C setpoint); input to the load calculation | Approved
TT-502 | 502 | RTD Pt100 temperature transmitter, in thermowell | CHW return header temperature | Return main (CHWR) | DC-I-001 | 0 | 30 | °C | 4-20 mA | Y | AI |  | In thermowell, tip in middle third of pipe; on return main upstream of the decoupler tee | CP-1 | TB-AI2-08 | Load calculation (delta-T) | Approved
FT-503 | 503 | Magnetic flow meter | Secondary loop flow | Secondary supply main (CHWS) | DC-I-001 | 0 | 30 | L/s | 4-20 mA | N | AI |  | >= 5D straight upstream, >= 2D downstream; pipe always full | CP-1 | TB-AI3-01 | Load calculation (flow x delta-T) | Approved
PDT-504 | 504 | Differential pressure transmitter | Secondary differential pressure at most remote CRAH (CRAH-1) | CRAH-1 supply / return branches | DC-I-001 | 0 | 200 | kPa | 4-20 mA | Y | AI |  | Taps across supply and return at CRAH-1, the hydraulically most remote coil | CP-1 | TB-AI3-02 | Secondary pump VFD control (80 kPa setpoint) | Approved
FT-505 | 505 | Bidirectional magnetic flow meter | Decoupler flow | Decoupler | DC-I-001 | -30 | 30 | L/s | 4-20 mA | N | AI |  | >= 5D straight on both sides (flow reverses); pipe always full | CP-1 | TB-AI3-03 | Reverse flow = stage-up signal | Approved
PT-506 | 506 | Pressure transmitter, with root valve | CHW supply header pressure | Primary supply header (CHWS) | DC-I-001 | 0 | 1000 | kPa | 4-20 mA | Y | AI |  | On primary supply header, with root valve | CP-1 | TB-AI3-04 | System pressure monitoring | Approved
LT-511 | 511 | Level transmitter | Expansion tank level | ET-1 | DC-I-001 | 0 | 100 | % | 4-20 mA | Y | AI |  | On ET-1 level connection | CP-1 | TB-AI3-05 | Detect water loss | Approved
PT-512 | 512 | Pressure transmitter, with root valve | System fill pressure at ET-1 | ET-1 connection | DC-I-001 | 0 | 600 | kPa | 4-20 mA | Y | AI |  | On ET-1 connection pipe, with root valve | CP-1 | TB-AI3-06 | Confirms system is filled and pressurized | Approved
LSL-513 | 513 | Level switch | Expansion tank low level | ET-1 | DC-I-001 |  |  |  | Dry contact |  | DI |  | On ET-1 low-level connection | CP-1 | TB-DI1-09 | Hardwired low-level alarm, independent of LT-511 | Approved
XV-601 | 601 | On/off actuated butterfly valve | WSE CHW isolation valve | WSE-1 inlet branch | DC-I-001 |  |  |  | 24 VDC |  | DO | FC | On WSE-1 inlet branch; actuator accessible | CP-1 | TB-DO1-03 | Mode switching (free cooling path) | Approved
ZSC-601 | 601 | Limit switch (closed) | XV-601 closed proof | XV-601 | DC-I-001 |  |  |  | Dry contact |  | DI |  | On XV-601 actuator | CP-1 | TB-DI1-10 | Prove the mode switch happened | Approved
ZSO-601 | 601 | Limit switch (open) | XV-601 open proof | XV-601 | DC-I-001 |  |  |  | Dry contact |  | DI |  | On XV-601 actuator | CP-1 | TB-DI1-11 | Prove the mode switch happened | Approved
TT-602 | 602 | Outdoor temperature sensor in radiation shield | Outdoor air temperature | Outdoor, north wall | DC-I-001 | -30 | 50 | °C | 4-20 mA | Y | AI |  | Shaded north wall, in radiation shield, away from exhausts and tower plume | CP-1 | TB-AI3-07 | Mode switching (wet-bulb calculation) | Approved
MT-603 | 603 | Humidity transmitter in radiation shield | Outdoor relative humidity | Outdoor, north wall | DC-I-001 | 0 | 100 | %RH | 4-20 mA | Y | AI |  | Shaded north wall, in radiation shield, away from exhausts and tower plume | CP-1 | TB-AI3-08 | Mode switching (wet-bulb calculation) | Approved

## Revisions
Rev | Date | Description
A | 2026-10-08 | Issued for review