## IO List
Point | Description | I/O Type | Signal | Source | Card | Channel | Terminal | Fuse | Spare
TT-112 | CH-1 evaporator leaving water temperature | AI | 4-20 mA | Instrument | AI1 | 1 | TB-AI1-01 | F-AI1-01 | N
TT-114 | CH-1 evaporator entering water temperature | AI | 4-20 mA | Instrument | AI1 | 2 | TB-AI1-02 | F-AI1-02 | N
TT-122 | CH-2 evaporator leaving water temperature | AI | 4-20 mA | Instrument | AI1 | 3 | TB-AI1-03 | F-AI1-03 | N
TT-124 | CH-2 evaporator entering water temperature | AI | 4-20 mA | Instrument | AI1 | 4 | TB-AI1-04 | F-AI1-04 | N
PT-211 | PCHWP-1 discharge pressure | AI | 4-20 mA | Instrument | AI1 | 5 | TB-AI1-05 | F-AI1-05 | N
PT-221 | PCHWP-2 discharge pressure | AI | 4-20 mA | Instrument | AI1 | 6 | TB-AI1-06 | F-AI1-06 | N
PT-311 | SCHWP-1 discharge pressure | AI | 4-20 mA | Instrument | AI1 | 7 | TB-AI1-07 | F-AI1-07 | N
PT-321 | SCHWP-2 discharge pressure | AI | 4-20 mA | Instrument | AI1 | 8 | TB-AI1-08 | F-AI1-08 | N
ZT-411 | TCV-411 position feedback | AI | 4-20 mA | Instrument | AI2 | 1 | TB-AI2-01 |  | N
TT-412 | CRAH-1 supply air temperature | AI | 4-20 mA | Instrument | AI2 | 2 | TB-AI2-02 | F-AI2-02 | N
TT-413 | CRAH-1 return air temperature | AI | 4-20 mA | Instrument | AI2 | 3 | TB-AI2-03 | F-AI2-03 | N
ZT-421 | TCV-421 position feedback | AI | 4-20 mA | Instrument | AI2 | 4 | TB-AI2-04 |  | N
TT-422 | CRAH-2 supply air temperature | AI | 4-20 mA | Instrument | AI2 | 5 | TB-AI2-05 | F-AI2-05 | N
TT-423 | CRAH-2 return air temperature | AI | 4-20 mA | Instrument | AI2 | 6 | TB-AI2-06 | F-AI2-06 | N
TT-501 | CHW supply header temperature | AI | 4-20 mA | Instrument | AI2 | 7 | TB-AI2-07 | F-AI2-07 | N
TT-502 | CHW return header temperature | AI | 4-20 mA | Instrument | AI2 | 8 | TB-AI2-08 | F-AI2-08 | N
FT-503 | Secondary loop flow | AI | 4-20 mA | Instrument | AI3 | 1 | TB-AI3-01 |  | N
PDT-504 | Secondary differential pressure at most remote CRAH (CRAH-1) | AI | 4-20 mA | Instrument | AI3 | 2 | TB-AI3-02 | F-AI3-02 | N
FT-505 | Decoupler flow | AI | 4-20 mA | Instrument | AI3 | 3 | TB-AI3-03 |  | N
PT-506 | CHW supply header pressure | AI | 4-20 mA | Instrument | AI3 | 4 | TB-AI3-04 | F-AI3-04 | N
LT-511 | Expansion tank level | AI | 4-20 mA | Instrument | AI3 | 5 | TB-AI3-05 | F-AI3-05 | N
PT-512 | System fill pressure at ET-1 | AI | 4-20 mA | Instrument | AI3 | 6 | TB-AI3-06 | F-AI3-06 | N
TT-602 | Outdoor air temperature | AI | 4-20 mA | Instrument | AI3 | 7 | TB-AI3-07 | F-AI3-07 | N
MT-603 | Outdoor relative humidity | AI | 4-20 mA | Instrument | AI3 | 8 | TB-AI3-08 | F-AI3-08 | N
SCHWP-1-SPDF | SCHWP-1 VFD speed feedback | AI | 4-20 mA | Equipment | AI4 | 1 | TB-AI4-01 |  | N
SCHWP-2-SPDF | SCHWP-2 VFD speed feedback | AI | 4-20 mA | Equipment | AI4 | 2 | TB-AI4-02 |  | N
SPARE | Spare channel (terminals installed) | AI |  |  | AI4 | 3 | TB-AI4-03 | F-AI4-03 | Y
SPARE | Spare channel (terminals installed) | AI |  |  | AI4 | 4 | TB-AI4-04 | F-AI4-04 | Y
SPARE | Spare channel (terminals installed) | AI |  |  | AI4 | 5 | TB-AI4-05 | F-AI4-05 | Y
SPARE | Spare channel (terminals installed) | AI |  |  | AI4 | 6 | TB-AI4-06 | F-AI4-06 | Y
SPARE | Spare channel (terminals installed) | AI |  |  | AI4 | 7 | TB-AI4-07 | F-AI4-07 | Y
SPARE | Spare channel (terminals installed) | AI |  |  | AI4 | 8 | TB-AI4-08 | F-AI4-08 | Y
TCV-411 | CRAH-1 chilled water coil valve | AO | 4-20 mA | Instrument | AO1 | 1 | TB-AO1-01 |  | N
TCV-421 | CRAH-2 chilled water coil valve | AO | 4-20 mA | Instrument | AO1 | 2 | TB-AO1-02 |  | N
CH-1-SP | CH-1 CHW supply temperature setpoint | AO | 4-20 mA | Equipment | AO1 | 3 | TB-AO1-03 |  | N
CH-2-SP | CH-2 CHW supply temperature setpoint | AO | 4-20 mA | Equipment | AO1 | 4 | TB-AO1-04 |  | N
SCHWP-1-SPD | SCHWP-1 VFD speed command | AO | 4-20 mA | Equipment | AO1 | 5 | TB-AO1-05 |  | N
SCHWP-2-SPD | SCHWP-2 VFD speed command | AO | 4-20 mA | Equipment | AO1 | 6 | TB-AO1-06 |  | N
SPARE | Spare channel (terminals installed) | AO |  |  | AO1 | 7 | TB-AO1-07 |  | Y
SPARE | Spare channel (terminals installed) | AO |  |  | AO1 | 8 | TB-AO1-08 |  | Y
FS-111 | CH-1 evaporator flow | DI | Dry contact | Instrument | DI1 | 1 | TB-DI1-01 |  | N
ZSC-113 | XV-113 closed proof | DI | Dry contact | Instrument | DI1 | 2 | TB-DI1-02 |  | N
ZSO-113 | XV-113 open proof | DI | Dry contact | Instrument | DI1 | 3 | TB-DI1-03 |  | N
FS-121 | CH-2 evaporator flow | DI | Dry contact | Instrument | DI1 | 4 | TB-DI1-04 |  | N
ZSC-123 | XV-123 closed proof | DI | Dry contact | Instrument | DI1 | 5 | TB-DI1-05 |  | N
ZSO-123 | XV-123 open proof | DI | Dry contact | Instrument | DI1 | 6 | TB-DI1-06 |  | N
XS-414 | CRAH-1 leak detection | DI | Dry contact | Instrument | DI1 | 7 | TB-DI1-07 |  | N
XS-424 | CRAH-2 leak detection | DI | Dry contact | Instrument | DI1 | 8 | TB-DI1-08 |  | N
LSL-513 | Expansion tank low level | DI | Dry contact | Instrument | DI1 | 9 | TB-DI1-09 |  | N
ZSC-601 | XV-601 closed proof | DI | Dry contact | Instrument | DI1 | 10 | TB-DI1-10 |  | N
ZSO-601 | XV-601 open proof | DI | Dry contact | Instrument | DI1 | 11 | TB-DI1-11 |  | N
CH-1-AL | CH-1 common alarm | DI | Dry contact | Equipment | DI1 | 12 | TB-DI1-12 |  | N
CH-1-ST | CH-1 run status | DI | Dry contact | Equipment | DI1 | 13 | TB-DI1-13 |  | N
CH-2-AL | CH-2 common alarm | DI | Dry contact | Equipment | DI1 | 14 | TB-DI1-14 |  | N
CH-2-ST | CH-2 run status | DI | Dry contact | Equipment | DI1 | 15 | TB-DI1-15 |  | N
CRAH-1-AL | CRAH-1 common alarm | DI | Dry contact | Equipment | DI1 | 16 | TB-DI1-16 |  | N
CRAH-2-AL | CRAH-2 common alarm | DI | Dry contact | Equipment | DI2 | 1 | TB-DI2-01 |  | N
PCHWP-1-ST | PCHWP-1 run status | DI | Dry contact | Equipment | DI2 | 2 | TB-DI2-02 |  | N
PCHWP-2-ST | PCHWP-2 run status | DI | Dry contact | Equipment | DI2 | 3 | TB-DI2-03 |  | N
SCHWP-1-AL | SCHWP-1 VFD fault | DI | Dry contact | Equipment | DI2 | 4 | TB-DI2-04 |  | N
SCHWP-1-ST | SCHWP-1 run status | DI | Dry contact | Equipment | DI2 | 5 | TB-DI2-05 |  | N
SCHWP-2-AL | SCHWP-2 VFD fault | DI | Dry contact | Equipment | DI2 | 6 | TB-DI2-06 |  | N
SCHWP-2-ST | SCHWP-2 run status | DI | Dry contact | Equipment | DI2 | 7 | TB-DI2-07 |  | N
SPARE | Spare channel (terminals installed) | DI |  |  | DI2 | 8 | TB-DI2-08 |  | Y
SPARE | Spare channel (terminals installed) | DI |  |  | DI2 | 9 | TB-DI2-09 |  | Y
SPARE | Spare channel (terminals installed) | DI |  |  | DI2 | 10 | TB-DI2-10 |  | Y
SPARE | Spare channel (terminals installed) | DI |  |  | DI2 | 11 | TB-DI2-11 |  | Y
SPARE | Spare channel (terminals installed) | DI |  |  | DI2 | 12 | TB-DI2-12 |  | Y
SPARE | Spare channel (terminals installed) | DI |  |  | DI2 | 13 | TB-DI2-13 |  | Y
SPARE | Spare channel (terminals installed) | DI |  |  | DI2 | 14 | TB-DI2-14 |  | Y
SPARE | Spare channel (terminals installed) | DI |  |  | DI2 | 15 | TB-DI2-15 |  | Y
SPARE | Spare channel (terminals installed) | DI |  |  | DI2 | 16 | TB-DI2-16 |  | Y
XV-113 | CH-1 CHW isolation valve | DO | 24 VDC | Instrument | DO1 | 1 | TB-DO1-01 |  | N
XV-123 | CH-2 CHW isolation valve | DO | 24 VDC | Instrument | DO1 | 2 | TB-DO1-02 |  | N
XV-601 | WSE CHW isolation valve | DO | 24 VDC | Instrument | DO1 | 3 | TB-DO1-03 |  | N
CH-1-SS | CH-1 start/stop command | DO | Dry contact (via interposing relay) | Equipment | DO1 | 4 | TB-DO1-04 |  | N
CH-2-SS | CH-2 start/stop command | DO | Dry contact (via interposing relay) | Equipment | DO1 | 5 | TB-DO1-05 |  | N
PCHWP-1-SS | PCHWP-1 start/stop command | DO | Dry contact (via interposing relay) | Equipment | DO1 | 6 | TB-DO1-06 |  | N
PCHWP-2-SS | PCHWP-2 start/stop command | DO | Dry contact (via interposing relay) | Equipment | DO1 | 7 | TB-DO1-07 |  | N
SCHWP-1-SS | SCHWP-1 start/stop command | DO | Dry contact (via interposing relay) | Equipment | DO1 | 8 | TB-DO1-08 |  | N
SCHWP-2-SS | SCHWP-2 start/stop command | DO | Dry contact (via interposing relay) | Equipment | DO1 | 9 | TB-DO1-09 |  | N
SPARE | Spare channel (terminals installed) | DO |  |  | DO1 | 10 | TB-DO1-10 |  | Y
SPARE | Spare channel (terminals installed) | DO |  |  | DO1 | 11 | TB-DO1-11 |  | Y
SPARE | Spare channel (terminals installed) | DO |  |  | DO1 | 12 | TB-DO1-12 |  | Y
SPARE | Spare channel (terminals installed) | DO |  |  | DO1 | 13 | TB-DO1-13 |  | Y
SPARE | Spare channel (terminals installed) | DO |  |  | DO1 | 14 | TB-DO1-14 |  | Y
SPARE | Spare channel (terminals installed) | DO |  |  | DO1 | 15 | TB-DO1-15 |  | Y
SPARE | Spare channel (terminals installed) | DO |  |  | DO1 | 16 | TB-DO1-16 |  | Y

## Summary
I/O Type | Instrument points | Equipment points | Total used | Card size | Cards | Installed channels | Spare | Spare % | Loop-powered
AI | 24 | 2 | 26 | 8 | 4 | 32 | 6 | 18.8 | 20
AO | 2 | 4 | 6 | 8 | 1 | 8 | 2 | 25 | 0
DI | 11 | 12 | 23 | 16 | 2 | 32 | 9 | 28.1 | 0
DO | 3 | 6 | 9 | 16 | 1 | 16 | 7 | 43.8 | 0
Total | 40 | 24 | 64 |  | 8 | 88 | 24 | 27.3

## Revisions
Rev | Date | Description
A | 2026-10-08 | Issued for review