## BOM
Item | Qty | Description | Manufacturer | Part No. | Rating | Tags / Drawing Ref | Notes
1 | 1 | Enclosure, NEMA 12, wall-mount, 1200 H x 800 W x 300 D mm, with backplate and bottom gland plate | TBD | TBD | NEMA 12 | CP-1 | Sized so every DIN rail row is at most 80% full
2 | 1 | Main circuit breaker, 120 VAC, 2-pole | TBD | TBD | 120 VAC, 10 A | CB | SCCR per UL 508A
3 | 1 | Surge protective device, 120 VAC | TBD | TBD | 120 VAC | SPD
4 | 3 | Power supply 24 VDC, DIN-rail | TBD | TBD | 5 A | PSU-1A, PSU-1B, PSU-2 | Clean bus redundant (2 units), actuator bus single
5 | 1 | Redundancy module 24 VDC (clean bus) | TBD | TBD | 2 x 10 A in | RM | Makes the clean bus redundant
6 | 1 | PLC CPU with Ethernet, BACnet/IP or Modbus TCP to BMS | TBD | TBD |  | CPU | PLC with interface to the building management system
7 | 4 | Analog input module, 8-ch, 4-20 mA | TBD | TBD | 8 ch | AI1-AI4 | From I/O list, 20% spare
8 | 1 | Analog output module, 8-ch, 4-20 mA | TBD | TBD | 8 ch | AO1 | From I/O list, 20% spare
9 | 2 | Digital input module, 16-ch, 24 VDC | TBD | TBD | 16 ch | DI1-DI2 | From I/O list, 20% spare
10 | 1 | Digital output module, 16-ch, 24 VDC | TBD | TBD | 16 ch | DO1 | From I/O list, 20% spare
11 | 11 | Interposing relay, 24 VDC coil, 1 C/O contact, with base | TBD | TBD | 24 VDC / 250 VAC 6 A | K1-K11 | DO used + 2 spare
12 | 26 | Fused terminal block with 5 x 20 mm fuse, 0.5 A | TBD | TBD | 0.5 A | F-AIx-xx | Loop-powered AI + AI spares
13 | 170 | Feed-through terminal block, 2.5 mm2 | TBD | TBD |  | TB-xx | From terminal count
14 | 40 | Ground (PE) terminal block, for cable shields | TBD | TBD |  | TB-xx S | AI + AO channels
15 | 1 | Ground bar, tinned copper | TBD | TBD |  | PE
16 | 24 | End plates, end stops and marker strips (sets) | TBD | TBD |  |  | 10% of terminals
17 | 3.6 | DIN rail 35 mm (m) | TBD | TBD |  |  | From layout
18 | 6.4 | Wire duct 40 x 80 mm with cover (m) | TBD | TBD |  |  | From layout
19 | 1 | Ethernet switch, unmanaged, 5-port, DIN-rail | TBD | TBD | 24 VDC | SW
20 | 1 | HMI touchscreen 10 in, door-mount | TBD | TBD | 24 VDC | HMI
21 | 1 | Pilot light, green, 24 VDC, "24 VDC ON" | TBD | TBD | 22 mm | PL
22 | 1 | Nameplates and wire markers (lot) | TBD | TBD
Manufacturer and part numbers are TBD until verified against manufacturer documentation.
PLC to be a modular family with 8-channel analog and 16-channel digital modules; if module sizes differ, the card count is recalculated.
Panel to be built by a UL 508A listed shop; SCCR marked on the nameplate.

## Fit check
Check | Value | Limit | Result
Terminals (installed incl. spares + power) | 236
Terminal row 1: TB-AI1, TB-AI2, TB-AI3 | 506 | 600 | Pass
Terminal row 2: TB-AI4, TB-AO1, TB-DI1 | 561 | 600 | Pass
Terminal row 3: TB-DI2, TB-DO1, TB-PWR | 589 | 600 | Pass
Vertical stack (mm) | 860 | 1100 | Pass
Backplate W x H (mm) | 700 x 1100

## Revisions
Rev | Date | Description
A | 2026-10-08 | Issued for review